## Slide 1: CSA Medical gas Standard
Registration, Installation & Inspection & Testing Requirements

## Slide 2: CSAZ7396.1 Medical Gas Standard
Standard is accepted in all Provinces and Territories in Canada and referenced in the National & Provincial Building Codes
Standard was written with the intent that a Medical Gas Inspection Body accredited by the Standards Council of Canada would test for all aspects of the Standard, except for pipeline pressure testing and anything that fell under the jurisdiction of CSA-B51
The intent is to have the Local Authority Having Jurisdiction ensure the pipeline and installers conform to CSA-B51 requirements

## Slide 3: CSAZ7396.1 Medical Gas Standard
As medical gas pipeline pressures range between 50-180 psi CSA-B51 mandates that the pipeline shall be registered as a pressure vessel and inspected by the authorized inspector or authority having jurisdiction
Gas pressures at this level installed with copper piping can be at the risk of rupture if not installed correctly and especially if incorrect fittings are used for installation
Since medical gases are installed throughout the hospitals leading to most patient rooms and operating rooms, it is critical that the piping complies with CSA-B51 in order to maintain patient and public safety

## Slide 4: CSAZ7396.1 Pressure requirement NEEDS and Expectations
All joints to be subjected to a 24-hour standing pressure test @ 150 psi or 1.5 times the maximum working pressure of the system
Pipeline systems are to be registered as a pressure vessel and need to carry a P-Number
All installers that complete brazing operations on gas piping, fittings and devices need to carry a Provincial Brazing Certificate
All companies that engage in installations of a medical gas system or projects need to have a Provincially registered Quality Control Program
All medical gas installers need to provide evidence of a valid Medical Gas License, meeting requirements of CSA Medical Gas Piping & Systems Installation Personnel Certification Program or equivalent

## Slide 5: Provincial Enforcement Variations
Identification, enforcement & recognition of Medical Gas Pipelines and systems as a “pressure vessel” vary greatly from Province to Province
CSAZ7396.1 Sub Committee would like to see a more uniform approach to ensure patient and public safety
The following slides are feedback from each Province, from the medical gas installation industry/contractors as per their work with the various Authority Having Jurisdiction (AHJ) representatives
Consideration of the substantial differences in approach to Medical Gas systems by each of the jurisdictions on Registration, Installation and Inspection requirements are identified

## Slide 6: NEWFOUNDLAND & lABRADOR
Newfoundland & Labrador has a proactive approach pertaining to Medical Gas systems as Pressure Vessels
Boiler Pressure Vessels department requires P-Numbers, Quality Control Program, Brazing Licenses and performance of on-site pressure test witnessing
In addition the Province requires any companies performing medical gas installations to apply specifically for a Provincial Medical Gas Contractor License, instead of a general contractor's license
Installers are required to be tested and registered with the Province and have a Brazing Log Book record of their current testing signed by the authority having jurisdiction

## Slide 7: New Brunswick
New Brunswick are very involved in Medical Gas Pipeline pressure vessel certification for systems
Boiler Pressure Vessels requires P-Numbers, Quality Control Programs, Brazing Licenses and performance of on-site pressure testing witnessing
In addition the Province requires any companies performing medical gas installations to apply for a Provincial Medical Gas Contractor License
Installers are required to have a New Brunswick Medical Gas License

## Slide 8: Nova Scotia
Nova Scotia requires a Brazing License and a Quality Control Manual only
Medical Gas Pipelines are not treated under the Boiler Vessel Act so a P-Number is not required and Pressure Tests are not witnessed by the Authority Having Jurisdiction

## Slide 9: Prince Edward Island
PEI has a Brazing & Licensing Program
Witnesses Pressure Tests
Does not require P-Number or Registration of Pipeline

## Slide 10: Quebec
Quebec requires a Brazing License
Pipeline is required to be registered
Quebec recently adopted the CSAZ7396.1 Medical Gas Standard and so they will be following its regulations once they complete their transition to the new code requirements

## Slide 11: Ontario
Ontario has a very well-run program administered by the TSSA as a third-party agency for ensuring compliance with regulations
Installers are required to have a valid Brazing License
Med Gas Pipelines required to be registered with a P-Number
Quality Control Manual is required
Pipelines are pressure tested and witnessed

## Slide 12: Manitoba
Requires Provincial Brazing License
Requires a Quality Control Program
Does not require P-Number Registration
Does not witness Pressure Test on site

## Slide 13: Saskatchewan
The Province recently initiated the requirement for a Brazing License
There is no requirement for treating Medical Gas Pipeline as a Pressure Vessel
No witnessing of pressure tests
No Quality Control Program required
No registration of P-Number required

## Slide 14: Alberta
No requirement for Brazing License
No requirement for P-Number registration
No Quality Control Manual required
No witness of pressure tests

## Slide 15: British Columbia
BC is not involved with Medical Gas Pipelines
It is not treated as a Pressure Vessel
No Brazing License is required
CSA-B51 is not enforced or recognized for Medical Gas Pipelines
Lack of enforcement is of concern as patient safety can be jeopardized due to unqualified Brazers using pipe & fittings not rated for the required pressures and having no understanding of the requirements for the system

## Slide 16: Northwest Territories
Does not require a Brazing License
Does not require P-Number Registration
Does not witness pressure test on site
Does not require a Quality Control Program

## Slide 17: Yukon
Does not require a Brazing License
Does not require P-Number Registration
Does not witness pressure test on site
Does not require a Quality Control Program

## Slide 18: Nunavut
Does not require a Brazing License
Does not require P-Number Registration
Does not witness pressure test on site
Does not require a Quality Control Program

## Slide 19: MEDICAL GAS CSA-B51 COMPLIANCE
There are only 3 Provinces in Canada that fully comply with CSA-B51 as it pertains to Medical Gas Pipelines
Medical Gas is not consistent or comparable in most jurisdictions in the Canadian compliance process for CSA-B51 Quality Control of systems
The chances of a serious incident resulting from a lack of inspection of medical gas pipelines as a pressure vessel are compounded by most patient beds are adjacent to 50-180 psi pipelines
Serious incidents happen years after a system has been completed as a result of poor installation techniques and improper fittings and piping and overall lack of cleanliness of material handling

## Slide 20: MEDICAL GAS CSA-B51 COMPLIANCE
Recommendations:
  Create an awareness for local Authorities having jurisdiction that Medical Gas Pipeline and systems falls under CSA-B51 and its requirements for identification, installation and testing/certification
  Identify this lack of compliance as an urgent need for public and patient safety across Canada
  In Provinces that choose not to inspect Medical Gas Pipelines an alternate solution should be found
  Ask Medical Gas Testing Agencies or private testing companies to become involved in development of a method to achieve the goal of compliance with CSA-B51
  Develop a solution that can address the problems identified with a real solution for change to the way it is currently being accomplished

## Slide 21: conclusion
In the interest of the safety of the patient and the general public who use hospitals and medical facilities every day where people go to be work, are tested, operated on, cured of illnesses, or just to visit their friends, we need collectively to make these places safe for them
We are ready to work with this group or its agencies or provincial jurisdictions, or whoever is needed, to elevate patient safety for Canadians, and create safer places by building a national compliance model for CSA-B51
We have discussed this with UA Canada and they have committed to helping us with this effort through their national network of specialty tradespeople towards building a better system

## Slide 22: Thanks for listening
Questions or Comments?
Discussion?
Recommendations?